## Read me
Cyber FAT / SAT punch list — KCH-CYB-PUNCH-001
Kanangra Creek Hydro Station · against CRS rev 0.2 and FAT plan KCH-CYB-FAT-001 rev 0.1 · DRAFT · 14 Sept 2026
THE ONE RULE THAT DECIDES WHETHER THIS LIST IS USEFUL
A HOLD POINT CANNOT BECOME A PUNCH ITEM. A hold point is a requirement whose failure stops shipment or stops energisation.
If it fails, the system is not accepted — it is not accepted conditionally with a note. The moment hold points start appearing
on this list, the list has become the mechanism by which the specification is quietly abandoned, and every subsequent signature
is worth less. Everything else may be carried here, with an owner and a date.
WHAT GOES ON THIS LIST
• DEFECT — a requirement is not met. The integrator fixes it. No commercial discussion is required; it was specified.
• DEVIATION — a requirement cannot be met as written. Requires disposition under CRS §15.1 BEFORE it is carried, not after.
• OBSERVATION — no requirement is breached, but something was seen that the asset owner should know. Carries no obligation
on the integrator. Observations are the most valuable rows on this sheet and the first ones deleted by someone tidying up.
WHAT AN ITEM MUST CARRY BEFORE IT IS ACCEPTED ONTO THE LIST
An owner who is a NAMED PERSON, a date, and an AGREED INTERIM POSITION. An item with a party but no person has no owner.
An item with no interim position is an unmanaged risk carried forward under the appearance of management — the plant runs
in the meantime, and something has to stand in the requirement's place until the fix lands.
THE PHASE BOUNDARY RULE
An item open at a phase boundary — FAT to shipment, SAT to energisation, commissioning to handover — is RE-DISPOSITIONED,
not rolled. Someone with authority looks at it again and decides, in the light of where the plant now is, whether it may
still be carried. Rolling is how a punch item becomes a permanent feature of the plant: it crosses three boundaries without
anyone deciding anything, and by handover it is indistinguishable from the design.
HOW TO USE
1. Yellow cells are inputs. Everything else is calculated — do not type a status count.
2. One row per item. An item covering two requirements is two items, because they will close on different dates.
3. "Closure evidence" is what a third party could use to confirm the fix. "Fixed" is not evidence.
4. The Summary sheet is the page that goes to the project meeting. Read AGE, not COUNT.

## Punch list
Punch list
Items arising from cyber FAT and SAT. HOLD POINT FAILURES DO NOT APPEAR HERE — they are defects that stop shipment or energisation and are resolved before the phase closes. Yellow cells are inputs.
Item | Raised at | Test case | CRS ref | Risk | Finding | Class | Agreed interim position | Corrective action | Party | Owner (named) | Due | Verify at | Status
P-01 | FAT | FAT-09 | CRS-054 | R-29 | Discovery protocol and vendor diagnostic web service listening on the DMZ protocol gateway as delivered. Both are outside the documented required service set. | Defect | Services blocked at the firewall pending removal. Blocking rule tagged for withdrawal so it is not carried into the as-built rule set as a permanent object. | Disable both services in the shipping configuration; reissue the configuration export and the required-set document. | Integrator | J. Marchetti | Before ship | FAT re-test | Open
P-02 | FAT | FAT-11 | CRS-010 | R-07 | Controller mode change alarms within 10 s when made through the engineering tool, but is SILENT when made at the front panel key switch. Requirement is path-independent. | Defect | Front-panel key switch physically locked; key held by the operations manager. Alarm on the engineering path continues to function. | Wire the key switch position to a monitored digital input and map it to the same alarm point. | Integrator | J. Marchetti | Before SAT | SAT | Open
P-03 | FAT | FAT-14 | CRS-013 | R-05 | Golden-copy comparison procedure exists and runs, but requires the controller to be taken to PROGRAM mode, which means it cannot be run on a generating unit. | Deviation | Comparison performed at each planned outage and after every logic download. Interval accepted as the exposure and recorded in the risk register against R-05. | Raise with the governor OEM as a product capability gap under CRS-051. Asset owner to decide whether to accept, or make it a condition of the next firmware revision. | Asset owner | R. Deng | SAT + 30 d | Document review | Open
P-04 | FAT | FAT-04 | CRS-044 | R-32 | Phishing-resistant MFA enforced. An SMS fallback path exists in the identity provider configuration but is not enabled for vendor accounts. | Observation | None required. Vendor accounts do not have the fallback enabled. | Recommend removing the fallback capability entirely rather than leaving it disabled, so that a future administrator cannot re-enable it without a change record. | Asset owner | R. Deng | Handover | Document review | Open
P-05 | SAT | SAT-04 | CRS-035 | R-26 | Eleven live unused ports found on control-zone switches at site, against three shown on the as-built. Port security is configured and refuses unauthorised devices. | Defect | Ports administratively disabled at the console the same day. Physical blockers not yet fitted. | Fit physical port blockers; reissue the as-built port schedule; add a port-count reconciliation to the annual review. | Integrator | S. Okonkwo | Before energise | Commissioning | Open
P-06 | SAT | SAT-07 | CRS-024 | R-18 | Full restoration demonstrated successfully. Measured recovery time 31 hours against an assumed 8 hours in the initial risk assessment. | Observation | None. The control works; the ASSUMPTION was wrong. | Update the consequence assumption behind S-09 and re-run the affected rows of the risk register. Reassessment trigger under approval record §8. | Asset owner | E. Zaré | Handover | Document review | Open
P-07 | SAT | SAT-02 | CRS-042 | R-30 | Automated firewall-to-conduit-register reconciliation implemented and running weekly. First run reported four undocumented flows, all legitimate and all absent from the conduit register. | Defect | Four flows documented in the conduit register as an interim as-built entry, pending formal revision of Annexure A. | Reissue CRS Annexure A conduit register at rev 0.3 including the four flows. GC-4 breach: a path that exists and is not registered is a defect regardless of exploitability. | Integrator | S. Okonkwo | Handover | Document review | Open
P-08 | SAT | SAT-09 | CRS-061 | — | Governor configuration supplied in the OEM's proprietary project format. No editable export available to the asset owner without an OEM licence seat. | Deviation | NONE AGREED. Escalated — this is one of the two requirements marked non-negotiable at CRS §15.2. | Escalate to contract. Either the OEM supplies an editable export, or the asset owner is licensed for the toolchain for the life of the asset at a price agreed now. | Asset owner | R. Deng | Before handover | Contract | Escalated

## Disposition rules
Disposition rules
Who may accept what, and for how long. Derived from the CRS and from the ZCR 4 acceptance authorities.
Class | What it means | Who disposes | Maximum carry | What closes it
Defect | A specified requirement is not met. No commercial discussion applies — it was in the specification and it was priced. | Integrator test lead accepts the item; asset owner witness accepts the interim position | To the next phase boundary, then re-dispositioned | Re-test of the original test case, witnessed. Not a statement that it was fixed
Deviation | The requirement cannot be met as written. May be a product capability gap (CRS-051) or a site constraint. | Asset owner, under CRS §15.1. NEVER the integrator alone | Life of asset if formally accepted; otherwise to the agreed date | A signed deviation record naming the compensating control and the accepting authority
Observation | No requirement is breached. Something was seen that the owner should know — often an assumption found wrong. | Asset owner engineering manager | No limit; review annually | A decision, recorded. An observation that is neither actioned nor consciously closed is the one that matters later
HOLD POINT failure | Not a punch item. Stops shipment or stops energisation. | Nobody. It is resolved, or the phase does not close | Zero | Re-test and pass. There is no other route
THE FAILURE MODE THIS SHEET EXISTS TO PREVENT
A punch item is dispositioned once, at the phase where it arose, and then travels. Nobody re-decides it, because re-deciding
requires someone to own the decision and the original owner has moved on. By handover the item has crossed three boundaries
without a single deliberate act, and it is now indistinguishable from the design. That is how plants acquire permanent
"temporary" firewall rules, standing vendor accounts, and key switches with the key left in.
The countermeasure is cheap and it is procedural: AT EACH PHASE BOUNDARY, EVERY OPEN ITEM IS READ ALOUD AND RE-DECIDED.
It takes twenty minutes and it is the difference between a punch list and a list of things that are now true about the plant.

## Summary
Punch list summary
Live-linked to the Punch list sheet. Nothing here is typed.
BY CLASS AND STATUS
Class | Open | Closed | Total
Defect
Deviation
Observation
Escalated
Total open
BY PHASE RAISED
FAT
SAT
Commissioning
READ THIS SHEET FOR AGE, NOT FOR COUNT
A count going down looks like progress and frequently is not. Items close in the order they are easy, so a list that starts
at twenty and reaches four has usually shed the four-hour fixes and retained the four that need a vendor, a contract or an
outage. Those four are the reason the list exists.
Ask three questions at every project meeting, and ask them in this order:
1. What is the OLDEST open item, and what has it been waiting for?
2. Which open items have crossed a phase boundary, and who re-decided them there?
3. Is anything on this list a hold point? If so, the phase did not actually close.
On this worked example, P-08 is the row to read. It is a deviation against CRS-061 — handover in editable source form —
with NO agreed interim position, escalated to contract. It is the cheapest item on the list to concede and the most
expensive to have conceded: a system the asset owner cannot maintain without the integrator is a system whose security
posture belongs to the integrator, for the life of the asset.